{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["Sheet1"],"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":31,"n_cols":6,"rows_kept":31,"merged":[[0,0,0,5],[1,0,1,5],[2,0,3,0],[2,1,3,1],[2,2,2,5],[4,0,16,0],[17,0,27,0],[29,0,29,5],[30,0,30,5]]}
["泰州学院济川校区监控、消防广播系统维保标准"]
["一、维保标准"]
["项目系统","维修保养检测内容","周期"]
[null,null,"每周","每月","每季度 ","每半年"]
["监控系统","监控服务器、存储阵列、核心交换机、汇聚交换机、编码解码器故障检查和排除","√",null,null,"√"]
[null,"服务器数据备份检查","√",null,null,"√"]
[null,"监控画面清晰度、角度检查","√",null,null,"√"]
[null,"视频存储是否满足不低于30天检查",null,"√",null,"√"]
[null,"线路所有接口、接头检查",null,{"v":0.2,"d":"20%"},null,{"v":1,"d":"100%"}]
[null,"室外支架、立柱、设备防雷检测",null,null,"√","√"]
[null,"室内机柜接地检测",null,"√",null,"√"]
[null,"前端摄像头除尘清洗",null,{"v":0.2,"d":"20%"},null,{"v":1,"d":"100%"}]
[null,"监控服务器、存储阵列、核心交换机、汇聚交换机、编码解码器、矩阵、监控大屏除尘保养",null,"√",null,"√"]
[null,"集中电源、UPS电源除尘保养",null,"√",null,"√"]
[null,"室外支架立柱除锈刷漆保养",{"$nulls":3},"√"]
[null,"现场各类设备、线缆及接口制作标签",null,{"v":0.2,"d":"20%"},null,{"v":1,"d":"100%"}]
[null,"监控系统全面检测",{"$nulls":3},"√"]
["消防广播系统","IP广播服务器主机（含服务器软件）、寻呼话筒、数控播放机、数控调谐器、消防输出模块故障检查和排除","√",null,null,"√"]
[null,"网络交换机（部分与监控系统合用）、网络分区解码器、强插音控器故障检查和排除","√",null,null,"√"]
[null,"单（多）通道音频解码器、前置放大器、输出功放故障检查和排除","√",null,null,"√"]
[null,"IP广播服务器主机（含服务器软件）、寻呼话筒、数控播放机、数控调谐器、消防输出模块除尘保养",null,"√",null,"√"]
[null,"网络交换机（部分与监控系统合用）、网络分区解码器、强插音控器除尘保养",null,"√",null,"√"]
[null,"单（多）通道音频解码器、前置放大器、输出功放除尘保养",null,"√",null,"√"]
[null,"各类吸顶、壁挂、柱式、草坪音箱故障检查和排除",null,{"v":0.2,"d":"20%"},null,{"v":1,"d":"100%"}]
[null,"室外支架、立柱、设备防雷检测",null,null,"√"]
[null,"室外支架立柱除锈刷漆保养",{"$nulls":3},"√"]
[null,"现场各类设备、线缆及接口制作标签",null,{"v":0.2,"d":"20%"},null,{"v":1,"d":"100%"}]
[null,"校园广播系统全面检测",{"$nulls":3},"√"]
[]
["二、更换设施设备标准"]
["1.监控系统设施设备更换：服务器、核心交换机、汇聚交换机、编码解码器、监控大屏等配件为原厂配件且不低于原有配置；存储阵列配件为原厂配件且不低于原有配置，存储硬盘为企业级海康专用硬盘，容量与原硬盘相同；摄像机像素不低于400万，且原球机、枪机、半球机型不变；前端光电交换机、光模块不低于原有配置；UPS电源控制器配件为原厂配件且不低于原有配置，电池为国内知名品牌，额定电压、容量不低于原有配置。                                                                                                 2.IP广播服务器主机（含服务器软件）、寻呼话筒、数控播放机、数控调谐器、消防输出模块、单（多）通道音频解码器、前置放大器、输出功放等配件为原厂配件且不低于原有配置。各类吸顶、壁挂、柱式、草坪音箱及配件为国内知名品牌，参数不低于原有配置。\n3.每半年（寒暑假期间）对监控系统和校园广播系统进行全面联动检测，出具三份全面完整的合格检测报告。\n"]